## Slide 1: TS#3 – July 4th – 8th Activities
K. Foraz

## Slide 2: General information
Material tractability @ point 1
Limited stay area- procedure in place
Lifts
  PM45 – HS all the week. Will we have a key problem ?
  PZ33 (generator) . HS from Monday to Wednesday
  For both access should be granted on Monday for the workers at 7h00
  Procedure for « urgent access » shall be written
RP survey
  Monday
  7h30-9h: Pt1-P5-P6 (up to 9h30) – P8
  9h30-11h30: P2-P4
  Tuesday
    7h30-8h30: P7
  Wednesday afternoon: P3

## Slide 3: Cryogenic
Cryo OK (provisionnal schedule)
  P2 : Thursday morning
  P4:
    Sector 45: no stop
    Sector 24: Thursday morning
    P6: no stop
    P8 (compressor): Friday night
Activities
  Cryo plant maintenance
  Cryo valves (less and less)
  Compressor at point 8

## Slide 4: EN-EL
Maintenance UPS (cf. planning) : UJ56 – RE48-RE52-RE58-RE32-UJ33-UA67-UA63-RE62
Point 1: FIP Radmon cabling
Point 2: thermoswitch cabling (no connection)
Point 5: FIP Radmon cabling
Point 6: UA63-UA67 cabling (additionnal interlocks)
Point 8:
  VDSL cabling- U86
  Laterla door on racks
  Provisionnal cabling CPU P8
  Cable trays in US85
TI2 : Fiabilisation of the emergency chain (no impact)

## Slide 5: EN-CV
Ventilation mode will be switch on Monday at 7h30, and back Friday at 18h
Ventilation maintenance at points 3, 5 & 8
Reduction of flow of waste water on the cooling towers – Monday, a priori no impact
Corrective maintenance on cooling towers SF2, SF4 et SF8 (M-T-W)
Point 8: Eletta & purge – no cooling water = M-T-W
Point 6: Pump exchange – no cooling water = M-T-W
Point 2: Purge – no cooling water = T-W-T
WR1842 :Access in TE80 via le TI8
UW : inspection

## Slide 6: TE-ABT
Point 2
  Replacement of a TMR in tank MKI
  Main Switch exchange on PFN C
  Removal of diagnostic units of RCPS on the interlock chain and direct connexion of the interlock (oil level transformer
  Check and tests of HT equipments
Point 8
  Proofness on 4 PFN inUA 87
  Removal of diagnostic units of RCPS on the interlock chain and direct connexion of the interlock (oil level transformer
  Check and tests of HT equipments
Point 6
  Replacement of entry boxes on MKB and MKD tanks
  Replacement of 2 generators MKD
  Re-calibration of generator MKDGA.JUA67
  Checks on signals (incorrect measures in MKD generators)
  Check and tests of HT equipments on MKD/MKB
  Checks on TCDQ

## Slide 7: TE-MPE
Upgrade of the DQAMC firmware related to mitigation of SEU events
Download firmware for quadrupole upgrade
Replacement of the power input switch on 500 DQHDS Quench Heater Power Supplies
Replacement of thermostats on DQRB’s: RR57 (3 units) and UA83 (3 units).
Temporary installation (and later removal) of 4 mDQQBS boards in S81 for a first validation of the new board for later use in the CSCM experiment Noise measurements and possibly powering of the two circuits to max. 100 A.
Firmware upgrade of fieldbus controllers type DQAMGND (for quench detection at current leads and total circuit voltage for RB, RQD and RQF) in order to overcome stalling problem.
Firmware update of all Q10/Q9 in order to fix a timing bug in PM
Tests ISRM
Powering tests of 60A from UA43 &UJ33

## Slide 8: EN-MME
Test tomographe in sector 81
Leak repair in sector 34
Works in lifts PM45 et PZ33
Lift maintenance
Removal of monorail at point 1
Etanchéité de l’UX65
US85 – cranes : corrective maintenance
UX65 crane : new cable
UX45- crane : brakers
GS-SEM
EN-MME

## Slide 9: EN-STI
Collimators:
  WR1801: Check the status of a sensor on the collimators TCLIB.6R2.B1 and TCL.5L1.B2
  Check several temperature probes of collimators (detailed list not yet defined)
RADMONs:
  WR1800: Installation and test of 2 new RADMONs in R542 et R562 (following installation by EN/EL of FIP cables and 230V outlets)
  WR1799: Data download/Adjustments/Inspection of RADMON in several areas (already known UJ13, UJ17, UJ56, RB44, RB46, RR73)
BE-BI
Installation of 4 new chambers at the level of the MKI@P2
Maintenance and upgrade of BSR, abort gap, longitudinal density & matching monitors
Upgrade BGI camera control system

## Slide 10: TE-VSC
LSS 6 - Exchange 4 primary pumps
LSS 2 – solenoid au niveau du Q6
LSS 2 – Functionnal test
LSS 7 - X-rays - 1/4 LSS per night
LSS 1, 2, 5, 8 - Evacuate condensed gas
LSS 8 – solénoïd
LSS 2 - X-rays
Secteur 45 – leak tests
Preventive maintenance of pumping groups
Test de turbo in warm areas

## Slide 11: BE-RF
Visual inspection & maintenance of RF equipment
Electronic boxes: Filtering and shielding (UFO’s sensibility)
Re-rooting of interlock lines related to fragile equipment on cavities (towards BIC) and revalidation of interlock systems
Cavities conditioning and loop checks
RF-ADT: new amplifiers
RF-ADT : checks on dampers and cavities ACS

## Slide 12: Foward detector
ATLAS ZDC et ATLAS-ALPHA: checks
ALICE ZDC: survey
CMS-FSC: upgrade
WR1855 :TOTEM: checks
Startpoint at point 8 (UA87)
IT
DGS-RP
RAMSES inspection et nouveau power supply (plus robuste)

## Slide 13: TE-EPC
RPHE.UA87.RQD.A81 : DIAGNOSTIC
  Problème : La chaine ID est donc actuellement interrompue au niveau du sous-convertisseur 3.
  Prévoir une intervention avec des câbles de rechange pour isoler le problème.
RPHGB.UA23.RQ6 : BAD CONTACTS
  Contact burndy enfoncée sur le cable SKDIAG OUT du sub-module Input 3 (fil marron du connecteur).
  Prévoir un remplacement du contact.
RPHGC.UA27.RTQX2.R2: OTHER INTERNAL FAULTS
  PROBLEM: Lost Sub-Converter 2 with OUTPUT MODULE 2 FUSE Fault
  ACTIONS: Change the Sub-Converter Number 2 modules.
RPHGC.UJ16.RTQX2.R : OTHER INTERNAL FAULTS
  Les fibres de RTQX2 avaient été contrôlés par Olivier Fournier et déclarés bonnes.
  Le problème de non réception de la trame pourrait venir du récepteur (FGC).
  ACTION : FGC à changer
RPLA.12R8.RCBH11.R8B2 : OTHER INTERNAL FAULTS
  PROBLEM: ANA_FLT warning: variation of the 3 PSU voltages.
  ACTION: Module to be changed.
RPLA.14R7.RCBH13.R7B1 : OTHER INTERNAL FAULTS
  PROBLEM: ANA_FLT warning: low -15V.
  ACTION: Module to be changed.
RPLA.16L1.RCBH16.L1B1 : OTHER INTERNAL FAULTS
  PROBLEM: ANA_FLT warning: low -15V.
  2011-06-10: psu_fgc = 5.06V, 15.07V, -14.447V @0.97A
  ACTION: Module to be changed.
  RPLA.16L1.RCBH16.L1B1 : OTHER INTERNAL FAULTS
  PROBLEM: ANA_FLT warning: low -15V.
  2011-06-10: psu_fgc = 5.05V, 15.07V, -14.44V
  ACTION: Module to be changed.
RPLA.16L8.RCBV15.L8B2 : OTHER INTERNAL FAULTS
  PROBLEM: ANA_FLT warning: low -15V.
  ACTION: Module to be changed.
RPLA.16R7.RCBV16.R7B1 : OTHER INTERNAL FAULTS
  PROBLEM: ANA_FLT warning: low -15V.
  2011-05-23: psu_fgc = 5.05V, 14.92V, -14.89V
  ACTION: Module to be changed.
RPLA.18R2.RCBH18.R2B1 : OTHER INTERNAL FAULTS
  PROBLEM: ANA_FLT warning: low -15V.
  2011-05-31: psu_fgc = 5.06V, 14.87V, -14.347V
  ACTION: Module to be changed.
RPLA.20L3.RCBV19.L3B1 : OTHER INTERNAL FAULTS
  Record created by Laurent Ceccone the 30/05/2011 at 16:36
  DCCT A Fault.

## Slide 14: GS-ASE
Maintenance :
  PAD-MAD PM45: M-T
  UJ27 – W
  MAD UJ23 – Th (repair)
  PAD- MAD PM76: F
Safety PLC @ P5
Check of electron stopper cabling
TIM cabling in US45

## Slide 15: Powering tests
Circuit | Test | Current | Length | Constraints | UPS | DFB concerned | Patrol | CRYO OK | Lock | When
RB.A67 | Verification new SW FGC | Up to 6 kA | 2-3 h | Powering phase II | P6 P7 | DFBAL DFBAM | P6 P7 P8 | A67 | NO | Wed
RQX.R1 | Reglage coefficients | nom | 2-3h |  | P1 P2 | DFBXB | P1 P2 | XR1 | NO | Thu
RQX.L2 | Reglage coefficients | nom | 2-3h | RD1.L2 operational | P1 P2 | DFBXC | P1 P2 | XL2 | NO | Thu
RCBCH10.R4B1 | R meas (MP3) |  |  | These tests will be done during the day with very low current and presence of people | P4 P5 |  | NO | A45 | NO | Thu afternoon
RCBCV8.R4B2 | R meas (MP3) |  |  |  | P4 P5 |  | NO | A45 | NO | Thu afternoon
RCBCV9.R3B2 | R meas (MP3) |  |  |  | P3 P4 |  | NO | A34 | NO | Thu afternoon
RCBCH7.R3B1 | R meas (MP3) |  |  |  | P3 P4 |  | NO | A34 | NO | Thu afternoon
RQ4.L5 RQ5.L5 RQ6.L5 RD2.L5 | ISRM meas (MP3) | ~3000 A | 5h | ElQA after PXI inst | P5 | DFBLD | P 4 5 6 | ML5 | DFBLD | Tue
RQ5.L6 | ISRM meas (MP3) | ~3000 A | 5h | ElQA after PXI inst | P6 | DFBMM | P 4 5 6 | ML6 | DFBMM | Wed
RQ4.R6 | ISRM meas (MP3) | ~3000 A | 1.5h | ElQA after PXI inst | P6 | DFBMM | P 6 7 8 | MR6 | DFBMM | Wed
RQ5.R6 | ISRM meas (MP3) | ~3000 A | 3h | ElQA after PXI inst | P6 | DFBMM | P 6 7 8 | MR6 | DFBMM | Thu
RQD/F maybe S45 -S12 - S23 | Multiple FPA | see sheet 2 | 6h |  | tbd | tbd | tbd | tbd |  | Thu if anything's available
RD34.LR3 | Cycle (EPC) | nom | 1 day | PC taken out from EIS (agreed with DSO) | P3 |  |  |  | NO | Mon
LHCb dipole | Trips inexpliques des convertisseurs | I_nom | 1 day | to be checked with the GLIMOS | P8 | n.a. | n.a. | n.a. | NO | 
Alice dipole | Vérifier les réglages des convertisseurs | I_nom | 1 day | to be checked with the GLIMOS | P2 | n.a. | n.a. | n.a. | NO | 
RPTL (Alice compensator) |  | I_nom | 1/2 day | to be checked with the GLIMOS | P2 | n.a. | n.a. | n.a. | NO | 
RB.A45 RQD/F.A45 | New DQQBS boards validation | 100 | 2-3 h |  | P4 P5 | DFBAH DFBAI |  | A45 | NO | Thu
RB.A56 | Quench propagation test | I_nom | tbd | Powering phase II | P5 P6 | DFBAJ DFBAK | P4 P5 P6 | A56 | NO | Wed & Thu