## Slide 1: RADIATION induced failures in LHC 28th June 2011
G. Spiezia (EN/STI/ECE) for RADWG/R2E

## Slide 2: Outline
  Strategy for the failure analysis
  Information Collection
  List of Failures per equipment
  Summary
  This is only a snapshot of the current situation. Full picture will be more clear in November after the R2E review

## Slide 3: Analysis Strategy
  Criteria to recognize a radiation failure:
  Failure occurs during beam-on/ collisions/losses (source of radiation)
  Failure is not reproducible in the lab or not clearly explained or recognized as ‘expected failure’
  Failure signature was already observed during radiation tests (CNRAD and others – if any ...)
  Failure frequency increases with higher radiation
  Further check: cross correlation with radiation detectors response at the moment of the failure

## Slide 4: Information collection and storing
  First information source: e-logbook, 8h30 LHC meeting
    High probability to miss failures which do not cause beam dump (Limitation1)
  Follow up of the suspicious events with the equipment owner (continuous mail exchange)
  What should be stored:
  Location
  Date-Time failure
  Component
  Consequence of the failure
  Where:
  RadWG list (see link)
  TE/CRG list (see link)
  TE/EPC list (see link)
  TE/MPE list (see link)

## Slide 5: Event Classification
  Confirmed radiation-induced failure
  To be confirmed
  Limitations and uncertainty sources:
    High probability to miss failures which do not cause beam dump
    Risk to include not-radiation induced failures
    Indirect failures on Equipment A due to equipment B. (e.g. Ethernet)

## Slide 6: List of Failures
  Collimation Control 2 Confirmed + 2 To be Confirmed
    Location: Ujs at point 1 and 5
    Type of failure: Abnormal reboot of the controller, memory corruption, Power supply failure
    Consequence: Beam dump
    Mitigation: Relocation/Shielding
    More Details
  Cryogenics Control (Cavern)PLCs: 3 Confirmed
    Location:US85
    Type of failure: PLC failures: 2 in QURCB cold box (same position) and 1 in the QURA
    Consequence: Beam dump (one case)
    Mitigation : Relocation
    More Details: 1, 2

## Slide 7: List of Failures
  Cryogenics Control (Tunnel) 4 Confirmed +1 To be Confirmed
    Location:UJ14, UJ56, UJ76
    Type of failure: Profibus Interface ET200s, Sipart PA positioners
    Consequence: Beam dump
    Mitigation : Relocation
    More Details: 1
  Cryogenics Control and readout on WORLDFIP – 2 Confirmed
    Location: Injection line TI2 (cell8L2-caused by a beam loss), RR53
    Type of failure: Block of the FIP communication, Digital Isolator
    Consequence: Beam dump (only for the Digital Isolator case)
    Mitigation : Software update to mask the digital isolator SEU and physical strap of the isolator to avoid change of range
    More Details: 1

## Slide 8: List of Failures
  Valve Controllers 0- Analysis on going ...
    Location: US85
    Type of failure: Trip of the valve positioners
    Consequence:
    Mitigation : Relocation already on going
  Biometry 2 To be Confirmed
    Location: Access port to UJ14 Uj16
    Type of failure: Block of the access system
    Consequence: Access to the tunnel delayed
    Mitigation : Relocation

## Slide 9: List of Failures
  WIC 1 Confirmed
    Location: Injection line TI8
    Type of failure: Deported I/O module failure
    Consequence: Beam dump
    Mitigation : Crate already moved (no failure since then).
  Power Converters 4 Confirmed 1 To be Confirmed
    Location: UJ14, RR17, UA87, UJ43
    Type of failure: AUX power supply failure(600A), AUX power supply(120A) (different signature)
    Consequence: Beam dump
    Mitigation: Shielding, Relocation, Redesign
    More Details: 1, 2

## Slide 10: List of Failures
  UPS 2 To be confirmed
    Location: UJ56, US85
    Type of failure: IGBT failure or control card failure
    Consequence: Beam dump
    Mitigation: Relocation
    More Details:
  QPS 39 Confirmed (23 cases were detected but are transparent to the operation) 6 to be confirmed.
    Location: LHC tunnel (93%), UJ14, Uj16, RR53
    Type of failure: Digital Isolator, MicroFip block, DSP, SDRAM block
    Consequence: Beam dump (6%), Lost of QPS ok(40%), Transparent to operation (50%). Magnet protection never lost
    Mitigation: Firmware update for the digital isolator (already implemented in 20%), automatic reset of microfip, new design
    More Details: 1

## Slide 11: QPS –details to explain

## Slide 12: QPS- details on the failures

## Slide 13: Continuous work ...
  Events to follow up in the last weekend
    PLC US85 -> + 1 case to be studied
    Cryo UJ56 -> + 1 case to be studied
    QPS uFIP -> Reiner talk for the details
    60A PC -> Analysis is on going...

## Slide 14: Failure rate over time
12 over 16 confirmed errors due to SEU happened in the weeks 16-23 (QPS is excluded)!

## Slide 15: Summary
Beam Dump or ‘visible’ for operation |  | 
Shielded area | Tunnel | 
14 | 3 | Confirmed
11 | 3 | To be confirmed
Other |  | 
Shielded | Tunnel | 
 | 15 | Confirmed
Transparent to Operation |  | 
 | 23 | Confirmed
QPS analysis
Detailed analysis for each case
Good visibility of events which caused the beam dump or remarkable stop
Other faults difficult to follow up (apart the detailed QPS analysis)
Snapshot picture (up to June 24th ). More statistics is required for a detailed analysis.
Projection on the those data (!Many sources of uncertainty!):
  If all the failures are confirmed: 31 errors 
  If factor 50 is used to scale with Lumi and same beam conditions are assumed (optimistic case) then one gets
  1500 errors per year due to radiation.
    Too many even if there is an error of a factor 10

## Slide 16: Summary – back up
Beam Dump or visible LHC stop |  | 
Shielded area | Tunnel | 
14 | 2+1 | Confirmed
8+3 | 3 | To be confirmed
Other |  | 
Shielded | Tunnel | 
 | 15 | Confirmed
Transparent to Operation |  | 
 | 23 | Confirmed
QPS analysis