## Slide 1: Beam induced heating assessment on LHC beam screens Arcs + DSs + ITs
L. Tavian
LBOC, 27 September 2011

## Slide 2: Assessment method (I)
Assessment of the mass flow using the flow characteristics of the BS loop control valves:
  Main issue: the rangeability R of the valves are not known ! (specified at 50 but a large dispersion suspected)
kv_max_Arc = 0.39 m3/h
kv_max_Arc34= 0.22 m3/h
kv_max_IT= 0.26 m3/h

## Slide 3: Assessment method (II)
Without beam (Qbs = 0)
  Enthalpy balance with Pc, Tc, Tout, QS & QEH allows to calculate m0
  m0, Pc, Tout, Pd, %, kv_max allow to calculate R
With beam:
  R, %, kv_max, Pc, Tout & Pd allow to calculate m (In some cases, possible cross-check by enthalpy balance with Pc, Tc, Qs, QEH and Tin : Thermal mass-flow meter)
  Enthalpy balance with m, Qs, QEH, Pc, Tc, Tout, allows to calculate Qbs

## Slide 4: What about: Pout= Pc (~3 bar) ?
Up to 100 W:
- OK for Arc half-cell (DP < ~5 % of Pc)
- Not true for IT loop (more iteration required!)
Reminder:
Arc half-cell: 4 capillaries in //
IT string: 2 capillaries in //

## Slide 5: Two typical behaviors for Arc and DS
29L6 left
15R5 right
Behavior with a power peak correlated with energy ramp
Behavior within expected
SR + IC loads (reduced power peak)

## Slide 6: Fill 1836 (02/06/2011): Arc + DS
Qbs (SR+IC scaled w/r to DR)
Qbs (SR+IC+EC scaled w/r to DR)
Half-cell
Half-cell with wrong BS type
Bunch spacing: 50 ns
Bunch number: 1092
Bunch length: 1.13 ns
Beam intensity: 1.27E14 p
Bunch intensity: 1.13E11 p
Some outliers w/r
to DR scaling

## Slide 7: Fill 1852 (05/06/2011): Arc + DS
Bunch spacing: 50 ns
Bunch number: 1092
Bunch length: 1.22 ns
Beam intensity: 1.29E14 p
Bunch intensity: 1.18E11 p
Qbs (SR+IC scaled w/r to DR)
Qbs (SR+IC+EC scaled w/r to DR)
Half-cell
Half-cell with wrong BS type

## Slide 8: Fill 2022 (12/08/2011): Arc + DS
Bunch spacing: 50 ns
Bunch number: 1380
Bunch length: 1.19 ns
Beam intensity: 1.79E14 p
Bunch intensity: 1.30E11 p
Qbs (SR+IC scaled w/r to DR)
Qbs (SR+IC+EC scaled w/r to DR)
Half-cell
Half-cell with wrong BS type

## Slide 9: Fill 2025 (13/08/2011): Arc + DS
Bunch spacing: 50 ns
Bunch number: 1380
Bunch length: 1.23 ns
Beam intensity: 1.86E14 p
Bunch intensity: 1.35E11 p
Qbs (SR+IC scaled w/r to DR)
Qbs (SR+IC+EC scaled w/r to DR)
Half-cell
Half-cell with wrong BS type

## Slide 10: Fill 2022 (12/08/2011): Sector 56 Beam induced heating on 52 BS (Arc + DS)
Peak correlated with energy ramp and/or bunch compression!
e-cloud? (but no energy and bunch-length dependence in scaling laws!)
Recovery of expected SR+IC loads after 1-2 hours!
 Correct BS impedance!

## Slide 11: Beam-induced heating: Scaling laws
Beam-induced load | Energy E | Bunch Population Nbunch | Bunch Number nbunch | Bunch Length σz [rms] | Beam-screen aperture b | Temp. Level
Synchrotron radiation | E4 | Nbunch | nbunch |  |  | BS
Image current | E0.5 | Nbunch2 | nbunch | σz-3/2 | b-1 | BS
Photo-electron cloud | ? | Nbunch3 | nbunch | ? | b-2 | BS
Beam gas scattering |  | Nbunch | nbunch |  |  | CM

## Slide 12: Rangeability distribution ? (416 valves (Arc + DS))
?
Specification !
Average: 32

## Slide 13: Location of valves having R > 40

## Slide 14: Heating with valves having R>40 Fill 2022 (12/08/2011)
Qbs (SR+IC scaled w/r to DR)
Qbs (SR+IC+EC scaled w/r to DR)
Half-cell
Half-cell with R > 40

## Slide 15: Fill 2022 & 2025 (12-13/08/2011): Inner Triplets
Fill 2022
Fill 2025
L1, R1
R2
L5, R5
L2
L8, R8
HL more correlated
to beam injection

## Slide 16: Steady state beam-induced loads according to the Design Report
Design Report data
Today for the ITs already a factor 1.3 to 2 w/r to the nominal values of the complete LSS (IT + MS) !
(but with a larger bunch population)
Local limitation due to valve size and BS pressure drop: ~150 W

## Slide 17: Beam-induced heating: Scaling laws
Beam-induced load | Energy E | Bunch Population Nbunch | Bunch Number nbunch | Bunch Length σz [rms] | Beam-screen aperture b | Temp. Level
Synchrotron radiation | E4 | Nbunch | nbunch |  |  | BS
Image current | E0.5 | Nbunch2 | nbunch | σz-3/2 | b-1 | BS
Photo-electron cloud |  | Nbunch3 | nbunch |  | b-2 | BS
Beam gas scattering |  | Nbunch | nbunch |  |  | CM

## Slide 18: Fill 1836: Inner triplets with nominal bunch population & 1092 bunches
Scaling to nominal beam (2808 bunches i.e. factor 2.6):
130 W ! (Just OK with local limitation)

## Slide 19: Conclusion
A new method is available for beam induced heating assessment on the LHC beam screens.
First analyses:
  Confirm the strong dependence of the peak value of beam induced heating with the bunch length.
  Do not show yet specific issues due to wrong beam-screen types in S34… but according to TE-VSC, BS saw-teeth are not efficient below 3.5 TeV.
  Confirm that extra transient heating (e-clouds? other?) is generated in the Arcs/DS by the ramp in beam energy. If this transient heating is due to e-clouds:
    Confirmation of the dependence of e-cloud w/r to beam energy and or bunch length.
    What about beam scrubbing scenario ? (today only at 450 GeV).
  Relax the worry about possible local impedance degradation (PIMs contacts,…).
  Confirm that, w/r to the Design Report, the beam induced heating is:
    For the Arc/DS: Well within the expected value scaled from the DR (if the bunch length is not too small – see fill 1836)… but the nominal bunch length is 1.06 ns
    For the Inner Triplets: Already above the nominal value (factor ~2) and at about 50 % of the local cooling limitation.
  Confirm that the rangeability of BS control valves is not very good (~30 in average for 50 specified).
    A distribution singularity still to be understood